很好，你现在已经把 **7 个核心模块**全部设计出来了。

我帮你 **按产品文档（Product Design Document / PRD）的结构重新整合**，并把之前写的内容全部串起来，**不遗漏内容、不打乱逻辑顺序**。

结构会按照一个 **标准能源 / Utility Platform 产品设计文档**来组织：

1. Product Overview

2. System Architecture

3. Core Modules（按顺序）

这样这份文档可以直接作为：

* 产品设计文档

* 项目方案

* 系统架构说明

* 投标技术方案基础

下面是 **整合后的完整产品文档（中文）**。

---

# Smart Utility & NetZero Platform

# 产品设计文档（Product Design Document）

---

# 1 产品概述

Smart Utility & NetZero Platform 是一个用于管理建筑能源与公用事业资源的综合数字化平台。

该平台通过接入各种设备表计（如电表、水表等），实现数据采集、能源分析、系统监控、告警管理、费用计费和报表输出等功能。

平台可应用于以下场景：

* 智慧园区

* 商业楼宇

* 工业设施

* 机场与交通设施

* 宿舍与租赁物业

系统通过统一的数据平台，实现对能源与水资源的 **实时监控、智能分析与运营管理**，帮助客户实现：

* 能源使用透明化

* 运维效率提升

* 成本管理优化

* 节能减排与 NetZero 目标

---

# 2 系统总体架构

系统整体架构可以分为五个层级：

```text

Device Layer

↓

Communication Layer

↓

Data Ingestion Layer

↓

Data & Analytics Platform

↓

Application Layer

```

各层级说明如下：

### Device Layer

包括各种现场设备：

* 电表

* 水表

* 网关

这些设备负责采集现场运行数据。

---

### Communication Layer

负责设备数据传输，支持多种通信协议：

* MQTT

* Modbus

* BACnet

* LoRaWAN

* Zigbee

---

### Data Ingestion Layer

负责接收设备数据并进行解析和标准化处理。

主要功能包括：

* 协议解析

* 数据清洗

* 数据验证

* 数据入库

---

### Data & Analytics Platform

负责数据存储与分析。

核心组件包括：

* Time-series database

* Data processing engine

* Analytics engine

* AI analysis engine

---

### Application Layer

应用层提供用户使用的业务功能模块：

1. Meter Onboarding & Reading Capture

2. Meter Location

3. Data Analysis & Historical Data

4. SCADA Map View

5. Alert Setting & Alarm Management

6. Billing

7. Report

---Part 1 — Meter Onboarding & Reading Capture

The Meter Onboarding & Reading Capture module is responsible for device onboarding, device management, and device data acquisition. It serves as the primary data entry module for the entire platform.、

Supported Communication Protocols

MQTT

Zigbee

Modbus

BACnet

Local Data Storage

Edge gateway shall store minimum one month of data

Data Synchronisation

Data shall be automatically synchronised after recovery

Virtual Meter

Use Cases

Total Energy Consumption per Floor

Total Energy Consumption per Building

Energy Consumption in Public Areas

Appliance Type Analysis    the system must support Appliance Type Tagging. Devices can be categorized by usage type, such as: Lighting Plug load Air conditioning

Part 2 — Meter Location

The Meter Location module is used to manage the spatial location of devices and establish the relationship between devices and the building spatial structure.

Hierarchy Data Model

Project

Block / Building

Floor

Room

Record GFA (including historical data)

Hierarchical Data Aggregation

After binding the hierarchy, the system can support automatic data aggregation.

Global Map View

Dashboard: Project location, Project status, Total consumption

lick on the project, will zoom into the project map, then display utility, include space for project discription such as address, size, etc, allow to click on different block, from block go to different floor, then go to different room then go to different device

Building Map / Floor Map

Device Map Display: Device Type, Status, Consumption

Device Movement

Device location history

Part 3 —  Data Analysis & Historical Data

The Data Analysis & Historical Data module serves as the core analytics component of the platform. Its primary role is to store, aggregate, analyze, and visualize data collected from devices.

Historical Data Management

The system must support long-term storage of device data and allow users to query consumption data over different time ranges.

Historical data must support the following time granularities:

Hourly usage

Daily usage

Monthly usage

Yearly usage

Custom period

Hierarchical Data Aggregation

the system must support a hierarchical spatial data model:

Device → Room → Floor → Block → Project

Utility Usage Analysis

The platform should provide Utilities Analytics to help identify opportunities for energy and water savings. A key feature is the Utility Usage Report, which allows users to view consumption data across different time intervals:

Hourly usage

Daily usage

Monthly usage

Utility Ranking

The system could generate a Utility Ranking Report. The platform should be able to identify:

Top energy consumers

Top water consumers

Ranking can be calculated across different dimensions, including:

Space

Usage tag

Consumption Benchmarking

The system should support Average Consumption Benchmarking (i.e. calculating average consumption values and comparing individual entities against those averages).

For example, a room’s energy consumption can be compared against:

The average consumption of other rooms on the same floor

The average consumption of other blocks within the same project

The average consumption of buildings of the same property type

If consumption significantly exceeds the benchmark, the system should flag the anomaly.

Example:

Room energy consumption+20% above average

The platform should display:

Percentage difference

Abnormal consumption indicator

Energy and Water Efficiency Index

The platform must calculate building efficiency indicators.

Energy Utilisation Index (EUI)

EUI measures the energy efficiency of a building.

The formula is: EUI = Energy Consumption / GFA

Unit: kWh / m²

The system must automatically compute EUI using historical energy consumption data.

Water Efficiency Index (WEI)

The system must also calculate the Water Efficiency Index (WEI).

WEI = Water Consumption / GFA

This metric helps evaluate water efficiency across buildings.

Historical GFA Support

The Excel requirements specify that the platform must maintain historical Gross Floor Area (GFA) records. This is necessary because building floor area may change over time.

Example:

2024 GFA = 5000 m²

2025 GFA = 5200 m²

The system must use the correct GFA value based on the timestamp when calculating EUI or WEI.

Data Visualization

The dashboards should support multiple visualization types and provide the following chart types:

Line charts (trend analysis)

Bar charts (comparison analysis)

Pie charts (distribution analysis)

Histograms

Heatmaps (usage consumption across spaces)

These visualizations can be used to display:

Energy consumption trends

Water usage trends

Comparative consumption across locations

Distribution of energy usage

Data Export

The platform must support exporting analytical data.

Users should be able to export data at different levels:

Device level

Room level

Floor level

Part 4 —  SCADA Map View

The SCADA Map View module provides a graphical interface for monitoring utility systems and device status in real time. This module enables operators to visualize the relationships between equipment, meters, and infrastructure using schematic diagrams, building layouts, and map-based interfaces.

Schematic Diagram (SCADA System Diagram)

The system should support schematic diagrams for electrical and water systems. These diagrams illustrate the flow of utilities through infrastructure.

For electrical systems, the platform must support electrical single-line diagrams. Typical components displayed include: Transformers Switchboards Distribution panels Circuit breakers Energy meters

Water systems should refer to PUB Water Balance Chart. Flow direction should be displayed to indicate upstream and downstream connections.

Device Visualization

Each device shown in the SCADA diagram should include real-time information.

Interactive Device Navigation

The SCADA interface could be interactive. Users should be able to click any device or meter icon in the diagram.

Alarm Visualization

The SCADA diagram must display alarm conditions and should use graphical indicators such as icons and colors to represent alarm status.

Device Health Indicators

The SCADA view must also reflect device health conditions, based on the Data Transmission Health Check module.

SCADA Diagram Editor

The platform should support an editable SCADA diagram interface.

Operators should be able to design or modify system diagrams using a graphical editor.

The editor should allow users to:

Add equipment symbols

Connect system components

Bind devices to diagram objects

Configure data points.

System Navigation Integration

The SCADA module must integrate with the platform's hierarchical navigation system. Users should be able to access SCADA views through the location hierarchy.

Real-Time Monitoring

The SCADA view must support real-time monitoring of device data.

Part 5 —  Alert Setting & Alarm Management

The Alert Setting & Alarm Management module is responsible for monitoring device status, detecting abnormal system conditions, and notifying operators when issues occur.

Threshold Alerts

The system must allow threshold values to be configured for each monitoring point.

Threshold alerts are triggered when measured values exceed predefined limits.

Each monitoring point may have multiple threshold levels.

Threshold alerts must also support configurable active periods.

Data Anomaly Alerts

The system could detect abnormal data patterns.

These alerts are triggered when data behavior deviates significantly from expected values. These alerts may be triggered automatically by the Data Analysis or AI analytics modules.

The platform should analyze historical data and identify deviations from normal behavior. Example thresholds include:1% deviation 5% deviation When abnormal consumption is detected, the system should trigger alert.

Alert Hierarchy

Alerts can be supported at different levels of the location hierarchy.

Alert Notifications

When an alert is triggered, the system must notify relevant users.

Supported notification channels may include:

Email, SMS, Web dashboard notification

Part 6 —  Billing & Utility Cost Management

Billing Models

Full Room Billing

Bed Billing

CAG: Bed Billing (Pure CE, Pure Non-CE, Mixed CE and Non-CE)

CE Contract - Monitor 3 months to come up with base consumption and bill excess consumption. Bill $40 per bill (fixed rate) over the base consumption for excessive consumption for that month.

Non-CE Contract - Consumption-Based Billing

Utility Rate History

The system should support configuring preset utility rates based on different time periods. All rate changes should be recorded with historical versions to ensure that billing calculations can always match the correct historical rate.