## Slide 1
Part 1 — Meter Onboarding & Reading Capture
Data Point according to project requirement
Supported Communication Protocols
MQTT
Zigbee
Modbus
BACnet
Local Data Storage
Edge gateway shall store minimum one month of data
Data Synchronisation
Data shall be automatically synchronised after recovery
Virtual Meter
Use Cases
Total Energy Consumption per Floor
Total Energy Consumption per Building
Energy Consumption in Public Areas
The Meter Onboarding & Reading Capture module is responsible for device onboarding, device management, and device data acquisition. It serves as the primary data entry module for the entire platform.
The system shall support Appliance Type Tagging, allowing devices to be categorized according to their usage type, such as Lighting, Plug Load, and Air Conditioning.
The platform shall provide analytics to break down and analyse energy consumption by appliance category. Example categories include Lighting energy consumption and HVAC energy consumption.
This functionality enables users to identify which systems or equipment types contribute the most to overall energy consumption and helps support targeted energy optimization and conservation strategies.

## Slide 2
Part 2 — Meter Location
Hierarchy Data Model
Project
Block / Building
Floor
Room
Record GFA (including historical data)
Hierarchical Data Aggregation
After binding the hierarchy, the system can support automatic data aggregation.
Global Map View
Dashboard: Project location, Project status, Total consumption
When a user clicks on a project from the global map view, the platform shall zoom into the selected project and display the project-level utility overview. The interface should include key project information such as project description, address, and total size (e.g., GFA).Users should be able to navigate through the spatial hierarchy by clicking progressively from Block → Floor → Room → Device, allowing detailed exploration of utility consumption and monitoring data at each level.
Building Map / Floor Map
Device Map Display: Device Type, Status, Consumption
Device Movement
Device location history
The Meter Location module is used to manage the spatial location of devices and establish the relationship between devices and the building spatial structure.

## Slide 3
Part 3 — Data Analysis & Historical Data
The Data Analysis & Historical Data module serves as the core analytics component of the platform. Its primary role is to store, aggregate, analyze, and visualize data collected from devices.
Historical Data Management
The system must support long-term storage of device data and allow users to query consumption data over different time ranges.
Historical data must support the following time granularities:
Hourly usage
Daily usage
Monthly usage
Yearly usage
Custom period
Hierarchical Data Aggregation
the system must support a hierarchical spatial data model:
Device → Room → Floor → Block → Project
Utility Usage Analysis
The platform should provide Utilities Analytics to help identify opportunities for energy and water savings. A key feature is the Utility Usage Report, which allows users to view consumption data across different time intervals:
Hourly usage
Daily usage
Monthly usage

## Slide 4
Part 3 — Data Analysis & Historical Data
The Data Analysis & Historical Data module serves as the core analytics component of the platform. Its primary role is to store, aggregate, analyze, and visualize data collected from devices.
Utility Ranking
The system could generate a Utility Ranking Report. The platform should be able to identify:
Top energy consumers
Top water consumers
Ranking can be calculated across different dimensions, including:
Space
Usage tag
Consumption Benchmarking
The system should support Average Consumption Benchmarking (i.e. calculating average consumption values and comparing individual entities against those averages).
For example, a room’s energy consumption can be compared against:
The average consumption of other rooms on the same floor
The average consumption of other blocks within the same project
The average consumption of buildings of the same property type
If consumption significantly exceeds the benchmark, the system should flag the anomaly.
Example:
Room energy consumption+20% above average
The platform should display:
Percentage difference
Abnormal consumption indicator

## Slide 5
Part 3 — Data Analysis & Historical Data
The Data Analysis & Historical Data module serves as the core analytics component of the platform. Its primary role is to store, aggregate, analyze, and visualize data collected from devices.
Energy and Water Efficiency Index
The platform must calculate building efficiency indicators.
Energy Utilisation Index (EUI)
EUI measures the energy efficiency of a building.
The formula is: EUI = Energy Consumption / GFA
Unit: kWh / m²
The system must automatically compute EUI using historical energy consumption data.
Water Efficiency Index (WEI)
The system must also calculate the Water Efficiency Index (WEI).
WEI = Water Consumption / GFA
This metric helps evaluate water efficiency across buildings.
Historical GFA Support
The Excel requirements specify that the platform must maintain historical Gross Floor Area (GFA) records. This is necessary because building floor area may change over time.
Example:
2024 GFA = 5000 m²
2025 GFA = 5200 m²
The system must use the correct GFA value based on the timestamp when calculating EUI or WEI.

## Slide 6
Part 3 — Data Analysis & Historical Data
The Data Analysis & Historical Data module serves as the core analytics component of the platform. Its primary role is to store, aggregate, analyze, and visualize data collected from devices.
Data Visualization
The dashboards should support multiple visualization types and provide the following chart types:
Line charts (trend analysis)
Bar charts (comparison analysis)
Pie charts (distribution analysis)
Histograms
Heatmaps (usage consumption across spaces)
These visualizations can be used to display:
Energy consumption trends
Water usage trends
Comparative consumption across locations
Distribution of energy usage
Data Export
The platform must support exporting analytical data.
Users should be able to export data at different levels:
Device level
Room level
Floor level

## Slide 7
Part 4 — SCADA Map View
The SCADA Map View module provides a graphical interface for monitoring utility systems and device status in real time. This module enables operators to visualize the relationships between equipment, meters, and infrastructure using schematic diagrams, building layouts, and map-based interfaces.
Schematic Diagram (SCADA System Diagram)
The system should support schematic diagrams for electrical and water systems. These diagrams illustrate the flow of utilities through infrastructure.
For electrical systems, the platform must support electrical single-line diagrams. Typical components displayed include: Transformers Switchboards Distribution panels Circuit breakers Energy meters
Water systems should refer to PUB Water Balance Chart. Flow direction should be displayed to indicate upstream and downstream connections.
Device Visualization
Each device shown in the SCADA diagram should include real-time information.
Interactive Device Navigation
The SCADA interface could be interactive. Users should be able to click any device or meter icon in the diagram.
Alarm Visualization
The SCADA diagram must display alarm conditions and should use graphical indicators such as icons and colors to represent alarm status.

## Slide 8
Part 4 — SCADA Map View
The SCADA Map View module provides a graphical interface for monitoring utility systems and device status in real time. This module enables operators to visualize the relationships between equipment, meters, and infrastructure using schematic diagrams, building layouts, and map-based interfaces.
Device Health Indicators
The SCADA view must also reflect device health conditions, based on the Data Transmission Health Check module.
SCADA Diagram Editor
The platform should support an editable SCADA diagram interface.
Operators should be able to design or modify system diagrams using a graphical editor.
The editor should allow users to:
Add equipment symbols
Connect system components
Bind devices to diagram objects
Configure data points.
Real-Time Monitoring
The SCADA view must support real-time monitoring of device data.
System Navigation Integration
The SCADA module must integrate with the platform's hierarchical navigation system. Users should be able to access SCADA views through the location hierarchy.

## Slide 9
Part 5 — Alert Setting & Alarm Management
The Alert Setting & Alarm Management module is responsible for monitoring device status, detecting abnormal system conditions, and notifying operators when issues occur.
Threshold Alerts
The system must allow threshold values to be configured for each monitoring point.
Threshold alerts are triggered when measured values exceed predefined limits.
Each monitoring point may have multiple threshold levels.
Threshold alerts must also support configurable active periods.
Data Anomaly Alerts
The system could detect abnormal data patterns.
These alerts are triggered when data behavior deviates significantly from expected values. These alerts may be triggered automatically by the Data Analysis or AI analytics modules.
Alert Hierarchy
Alerts can be supported at different levels of the location hierarchy.
Alert Notifications
When an alert is triggered, the system must notify relevant users.
Supported notification channels may include:
Email, SMS, Web dashboard notification
The platform should analyze historical data and identify deviations from normal behavior. Example thresholds include:1% deviation 5% deviation When abnormal consumption is detected, the system should trigger alert.
短信平台费用？

## Slide 10
Part 6 — Billing & Utility Cost Management
The Billing module is responsible for calculating utility charges based on consumption data collected from meters and allocating costs to tenants, rooms, or beds depending on the billing model.
Billing Models
Full Room Billing
Bed Billing
CAG: Bed Billing (Pure CE, Pure Non-CE, Mixed CE and Non-CE)
  CE Contract - Monitor 3 months to come up with base consumption and bill excess consumption. Bill $40 per bill (fixed rate) over the base consumption for excessive consumption for that month.
  Non-CE Contract - Consumption-Based Billing
Utility Rate History
The system should support configuring preset utility rates based on different time periods. All rate changes should be recorded with historical versions to ensure that billing calculations can always match the correct historical rate.

## Slide 11
Part 7 — Report
System Availability Report
Data Unavailability Report
Part 8 — Login MFA
Email OTP